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Sample: Same as above. Typically 400 Amp Hour capacity. For example 12 volt batteries with top or front mount terminals mounted on a multiple rack shelves.
APS is proposing the East Penn/Deka Unigy I 12AVR200ET Battery.
The solution uses 2 strings in parallel of 4 12 VDC batteries in series to achieve 400 AH at 48 VDC. 
Exclusive IPF® technology optimizes power capacity, cell consistency, and long-term reliability.
Front access design for easy installation and maintenance.
Space saving Absorbed Glass Mat (AGM) construction (48 volt system fits in 23" racks).
Reinforced case resists bulging and meets safety requirements (UL94 V-0).
Computer-aided design and manufacturing control processes and standards to ensure quality products.
Batteries meet or exceed IEEE 485 and Telcordia capacity requirements.
Battery design and construction meet UL recognition requirements.

SPECIFICATIONS 
Nominal Voltage: 12-Volt/200 ampere-hours @ 8 hr. rate to 1.75 final volts/cell
Positive Plate: Pure lead, low-calcium, high-tin alloy
Negative Plate: Lead calcium alloy
Post Seal: Epoxy-sealed
Terminal: Front access, 1/4" - 20 threaded insert
Container: Flame-retardant, polypropylene -
UL 94 V-0/>28% L.O.I.
Safety Vent: Low positive pressure, self-sealing w/ flame arrestor
Float Voltage: 2.25 volts per cell ± 0.01 vpc
(Range: 13.44 to 13.56 volts per 6-cell unit)
Battery Life: 10 years in float
applications at 77°F/25°C
Dimensions: 24.30" (617.2 mm) L x 4.97" (126.3 mm) W x 12.74" (323.6 mm) H
Weight: 151 lbs. (68.5 kg)

The East Penn battery is manufactured in the USA at the factory in Lyon PA.
The 12AVR100ET battery carries a 4 year full and 6 year Pro Rata warranty for a total warranty period of 10 years.
