ExhibitB2-DCPowerSystemsLgSolutionNarrative

### Based on the sample provided 
DC Power System: Sample Scenario, Large Solution

### Sample: As above but capable of charging and maintaining a 800 Amp Hour battery bank. A typical example would be 12 volt batteries, or a large 2 volt battery array wired for 48 volts. Will typically use a larger 19” or 23” seismic rack due to battery weight.

The solution is from Delta/Eltek Power It is the Unity series. This specific model is 10 RU high, has 8 rectifiers positions, 21 load breaker positions, 3 Bulk Load Positions, 5 Bulk battery output connections on a Shunt and LVD to support external Battery racks. This System has 19 additional breaker positions to support a 24 or 12 VDC load. Equipped with (5) 3000 watt rectifiers, this solution can power the 800 AH battery and still leaving 60 amps for the load with N+1 redundancy and room to add up to 3 additional rectifiers for future growth. Maximum recharge current of a lead acid battery should never exceed 25% of its rated AH capacity (200 amps in the case of an 800 AH Battery) to prevent over charging of the battery which will lead to battery damage and a shortened service life.

This can be mounted in a 19” rack and the controller has all of the features that a modern power system offers. No special software is required to access the built in web interface.

For a real world scenario, we would speak to the customer/engineer to determine the following items to correctly size the power system and battery.

- What is the Site load?

- What is the desired runtime on battery? This along with the site load will determine the correct battery size.

- What is the available AC power? This will help to determine the maximum size of the rectifier that can be used.

- What is the desired battery recharge time? This along with the AC Power and site load determines the rectifier size and quantity.

- What are the distribution requirements? This will determine the type, size and quantity of distribution fuses or breakers.

- Are there and any space issues at the site? This will help determine the rack size and the battery type (12 volt vs 2 volt) that can fit in the site.

If the customer needs installation we will ask the following questions

- Where is the site located?

- Is there a site drawing or can we perform a site walkthrough?

- What are the site conditions/constraints? IE: Mountain top, rooftop, in a secured facility, 4x4 access only, etc.

- Are there any specific work hours?

- Will there be a site escort, or will we be provided access?

- What is the scope of work? Will we be transferring any loads? Will we be running equipment load cables?

Once an order has been received, if we are performing the installation, we will have the equipment shipped to one of our warehouses for inspection of completeness and any shipping damage. If needed, we can also integrate DC power equipment from different manufacturers into a system prior to installation. We will then coordinate with the site contact to schedule the installation. If we are not performing the installation, we can ship directly to whatever facility the customer prefers.

Once on site our technicians will verify site conditions and before any work begins, they will hold a tailgate safety meeting. If this is a new site, the batteries and DC power system will be installed in the designated location. The batteries will be cabled and connected to the DC system and the DC power system will be connected to the customer supplied AC power. Once these connections have been made and verified the DC power system will be turned up according to the manufacturer’s instructions. APS will verify the system function and voltages before either leaving the site or transferring loads. Alarm cables will also be ran at this point and a network cable can be installed to the customer network for remote monitoring and access.

If this is an existing site and loads need to be transferred from an older power system to the newer one we would electrically tie the old and new plants together to reduce voltage potential and then transfer the loads by either turning off the breaker and moving the wire on loads that can be turned down or by performing a hot cutover  by splicing the cables using a compression H-Tap to install a new wire to the new system and then remove the old wire from the old system and cut it off at the H-Tap, then install a safety cover over the H-Tap. This will be repeated for each load to be transferred.

After the loads have been transferred, we will remove the old power system from the site to either transport it back to the customer warehouse or back to our facility for disposal and recycling.

APS will also install a temporary battery to supply battery backup while the main site batteries are being changed out. Old batteries will be removed from site and transported to APS facility for proper disposal at an approved EPA certified smelter.

If purchased a battery monitor will be installed on the battery and, depending on the manufacturer, be connected to the power system or to the customer network.

| QTY | Part Number | Description |
| --- | --- | --- |
| 1 | UNT20810.00013 | UNITY POWER SYSTEM WITH FLATPACK2 - 48V, 500A POWER SHELF - RECTIFIER POSITIONS: QTY 8 (SUPPORTS BOTH 2000W and 3000W RECTIFIERS) - INPUT CONNECTIONS: REAR ACCESS TO AMP CONNECTORS, ONE INPUT PER RECTIFIER PRIMARY DISTRIBUTION: 19" WIDE, NEGATIVE VOLTAGE OUTPUT QTY 21 CIRCUIT BREAKER POSITIONS (CBB STYLE) 1/4"-20 STUD 5/8" CENTER -QTY 21 LOAD BREAKER POSITIONS QTY 3 BULK LOAD POSITIONS -QTY 1: 3/8"-16 NUTS ON 1" CENTER -QTY 2: 1/4"-20 NUTS ON 5/8" CENTER BULK BATTERY POSITIONS THRU A SHUNT & LVBD -QTY 5: 3/8"-16 STUDS ON 1" CENTER OR QTY 5: 1/4"-20 NUTS ON 5/8" CENTER SECONDARY DISTRIBUTION: -QTY 19 CIRCUIT BREAKER POSITIONS (CBB STYLE) 1/4"-20 STUD 5/8" CENTERSMARTPACK S PANEL MOUNT CONTROLLER INCLUDED SPSP-UNT600-A01 |
| 5 | 241119.105.VC | FLATPACK2 HE RECTIFIER 3000W 48V, -INPUT: 85-305VAC; FAN COOLED (FRONT TO BACK); -OUTPUT: 3000W @ 176-305VAC, 3000W @ 176VAC LINEARLY TO 1382W @ 85VAC. -EFFICIENCY: >96.2%; -OPERATING TEMPERATURE: -40 TO +45°C: 3000W; LINEARLY DERATE FROM 3000W @ 46°C TO 2100W @ 75°C; SHUTDOWN AT 75°C, AUTOMATICALLY RESTART AT LOWER TEMPERATURE -STORAGE TEMPERATURE: -40 TO +85°C -DIMENSION & WEIGHT: 4.29"W x 1.69"H x 13"D; 4.3 LBS |
| 3 | 331E23640800 | BLIND PANEL FP2 HE BLACK G1 |
| 5 | LA1010-UU | LINE CORD WITH AMP MATE-N-LOCK CONNECTOR AT ONE END AND UNTERMINATED AT THE OTHER END, 10AWG CABLE, 10' LONG |
| 2 | 504934 | CABLE 4P ALARM FLATPACK MCU 50FT ***MUST ORDER TWO PC FOR SMARTPACK CONTROLLER*** |